## Slide 1: Grid Edge Time Synchronous Measurement & Applications
Yilu Liu (Liu@utk.edu)
University of Tennessee, Knoxville
Oak Ridge National Laboratory

## Slide 2
Partial list of UTK/ORNL sensor locations in US/Canada
Notes: FNET, the frequency monitoring network is such a wide-area measurement system that monitors the North American power grids. The sensors, called Frequency Disturbance Recorders, are taking GPS-synchronized frequency, voltage and phase angle measurements at 120 V outlets and send them via internet to the central servers here at Whittemore. Various applications have been developed to improve situation awareness, such as event triggers, disturbance location estimations. My work is also based on the wide-area measurements from FNET. (next)

## Slide 3: Worldwide Monitor Deployment Map (UTK)

## Slide 4: Disturbance Propagation Playback 2-26-08

## Slide 5
On-line Event Location -TDOA
US Patent: 7519454,7765034

## Slide 6: Sample automatic event alert
Event Estimation:
640MW EI Generator Trip at 20:28:00UTC, on 09/09/2014 near Paradise power plant (SERC)
((Muhlenberg,KY,42337; Latitude: 37.2578, Longitude: -86.9792)
PLEASE KEEP THIS INFORMATION CONFIDENTIAL.

## Slide 7
Forced Oscillation Detection
  Detection of forced oscillation
  Step 1) Detection of abnormal envelope height of phase angle
  Step 2) Find the dominant mode.
  Confirmed Forced Oscillation Cases
  B. Start from 2016-06-17 07.12.40, EI
  A. Start from 2016-11-27 05.51, EI

## Slide 8: Recent Major Forced Oscillations

## Slide 9: Measurement Derived Grid Model for Oscillation Damping
Winter
Summer
Control effect in Terna Grid
Control effect on CURENT HTB
Real-time data-driven model based oscillatory mode representation
Apply to NAPA, TERNA, and Saudi Grids
Demonstrate on CURENT HTB
Realtime updated Grid transfer functions
Notes: ERC work now moved to industry applications

## Slide 10: Case Study - Terna Grid Oscillations
Developed the controller using measurement-driven model
Terna: TSO in Italy
Mode #1
Z8
Z7
Z1
Z4
Mode #2
Mode #3
Z13
Z1: Bosnia & Herzegovina
Z4: Hungary, Z7: France
Z8: Germany,
Z13: Italy - Palermo
0.25Hz oscillation detected by FNET/GridEye on May 21, 2018

## Slide 11: Case Study - NYPA Grid
Transfer function model was constructed by utilizing measurements.
Utilized the measurement-driven model to design oscillation damping controller.
Area map of New York State grid
Source: NYISO
UsNyLeroy667
UsNyFulton826
Oscillation detected by FNET/GridEye

## Slide 12: Case Study - SEC Grid
COA
EOA
NOA
WOA
SOA
FDR #1191(COA)
FDR #1509 (WOA)
FDR #1191 - #1509
Modal analysis (five operation areas)
Transfer function model development & controller design
0.32Hz oscillation detected by FNET/GridEye on May 16, 2018
FDR #1191
FDR #1509

## Slide 13: Detect FIDVR (Fault Induced Delay of Voltage Recovery)

## Slide 14: Islanding Detection of Bulk Grid & Micro Grid
Case 1 (EI 09/18/2007 10:21:23 UTC)
Case 2 (WECC 06/01/2010 23:37:32 UTC)
Fig. 1
Fig. 2
Fig. 3
Fig. 4

## Slide 15
Grid  UPS  Grid Detected
On UPS
Off Grid Detection for Hospitals and Data Centers

## Slide 16: Line Trip Detection and Location
Raw angle
Unwrap angle
LP filter (mean)
Peak detection
Trigger report
+
-
LP filter (median)

## Slide 17
Angle Stability using Relative Angles
Center-of-Inertia (COI) angle vs the rest of the bus angles

## Slide 18: Interconnection Inertia Monitoring
EI
WECC
ERCOT
QUEBEC
Possible inertia
estimation based on
local frequency!
Notes: The graph depicts actual data from events in the NERC dataset.
Note the direct relation between resource loss and ROCOF and the higher ROCOF in the smaller interconnections.
Events that diverge significantly above the regression line are likely lower inertia events (could also be measurement error misreported event size).
Events significantly below the line might be higher inertia events, but are more likely “slow unit trips” (e.g. runbacks prior to the trip)
If inertia were to decline year over year, the regression line for the interconnection would rotate counter-clockwise.
The graphs above are raw ROCOF. You could get normalized ROCOF by projecting a perpendicular line up from the 1000MW point on the x axis.
To track inertia over time, NERC shuld track normalized ROCOF by Interconnection year over year.

## Slide 19: Dynamic Model Validation - Eastern Interconnection
Measurement in MA Measurement in FL
Measurement in OH Measurement in KS
Case Study: a 1100 MW Generation Trip in North Carolina
Improved model accuracy
Synchrophasor measurement collected by FNET/GridEye is used to calibrate the simulated frequency response.
Governor deadband is adjusted to reflect the actual system performance.

## Slide 20: Synchronized Point-on-Wave (SPOW) from Mobile UGA
Mobile Universal Grid Analyzer
Voltage from phase-to-ground fault
GPS time-indexed sample data

## Slide 21: Real-Time Signal-to-Noise Ratio Estimation
Real-time SNR estimation with wall signal at different SNR window sizes
Real time SNR measurement with Signal generator
(a) 20dB reference; (b) 40dB reference (b) 60dB reference
Project Goals:
Implement SNR algorithm in the UGA for real-time SNR estimation
HTB needs driven

## Slide 22: New Deployment - Puerto Rico Grid

## Slide 23: Related web links:
FNET Live Display : http://fnetpublic.utk.edu/gradientmap.html
How to install FDR: http://www.youtube.com/watch?v=9Vt2OlVoBJc&NR=1
Sample oscillation alert:
http://fnetapp.eecs.utk.edu/FNETOsciEventReport/20120110_202749_EI_OsciSummary.html
FL Event Movie; http://www.youtube.com/watch?v=bdBB4byrZ6U&feature=related
CA Blackout Movie: http://www.youtube.com/watch?v=YsksUyeLu2Y
April 27 Storm TVA line trip Movie: http://www.youtube.com/watch?v=KmK2VMG57gw&feature=related
2011 Virginia Earthquake Movie: http://www.youtube.com/watch?v=XUN_h-k8kBg&feature=related
2003 blackout movie: http://www.youtube.com/watch?v=eBucg1tX2Q4&feature=related
Worldwide Measurement Map: http://powerit.utk.edu/worldmap/
UTK PowerIt Lab: http://powerit.utk.edu
NSF/DOE Center: http://curent.utk.edu